## BOQ
PROJECT : KFC , AHMEDABAD AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
PROJECT : KFC , AHMEDABAD AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | Hi Side Works
1 | Air Handling Units (Indoor Type)
Supply , Installation , testing & commissioning Of Double skin Floor mounted / Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG/m3 , Plug Fans / DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU's installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI / Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of AHU Technical Data by consultant prior to fabrication is required.
Design Parameters- 25 deg C -R.A.Temp, 55% RH, 9 deg C- CHW IN
Water Flow Rate- 2.4 GPM/ TR
1.1 | Ceiling Suspended Type
1.1.1 | 3400 CMH(2000 CFM)at 30 mm External Static Pressure, 6 RD Cooling Coil, Approx 5.0 TR, 1 x 1.1 KW Motor | Nos | 1 | 235000 | 235000
1.2 | Digital Heating/Cooling Thermostat for Air Handling Units | Nos. | 1 | 14500 | 14500
2 | Kitchen Scrubber (Dry Type)-With Fan Section
2.4 | Accessories
The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt & pulleys, vibration isolators, internal frame works ,canvas connection, Inlet/Outlet flange connection etc
| 8500 CMH (5000 CFM) DIDW Blower Capacity at 80 MM ESP 3.75 KW (3 Phase) motor | Nos | 1 | 230000 | 230000
3 | Treated Fresh Air Handling Units (Indoor Type)
Supply , Installation , testing & commissioning Of Double skin Floor mounted Type Treated Fresh air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG/m3 , Plug Fans /DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the TFA's installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI / Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of TFA Technical Data by consultant prior to fabrication is required. The TFA shall have Thermal Break Profile .
3.1 | Ceiling Suspended Type
3.1.1 | 3740 CMH (2200 CFM) at 30 mm Static Pressure, 6 RD Cooling Coil, Approx 12 TR, 1 x 1.1 KW Motors | Nos | 1 | 67000 | 67000
4 | AHU Fan Section
4.1 | Supply, Installation, Testing and Commissioning of Double Skin Type AHU Fan section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside with 25mm injected PUF insulation of 38KG/m3 , G.I. blower section, VFD Operated Plug Fans with motors , base , drive arrangement ,Filter, motor drive suitable for Outdoor Application complete as per specifications and drawings .
4.1.1 | 2000 CFM (with Backward Curve Type DIDW Blowers 1.1 KW Motor ; ESP 30 mm of wg;for Toilet Exhaust | Nos | 1 | 55000 | 55000
| Sub-Total Part-'A' Rs. |  |  |  | 601500
Part B | DX UNITS
1 | Air Cooled Split units (Minimum 4-Star rated and latest in present year
1.1 | Supply , Installation , testing and comissioning of Air Cooled Split airconditioners each comprising an outdoor unit consisting of Inverter compressor, air cooled condensing unit, Condenser fan etc. with outer casing and indoor fan coil unit(s) consisting of centrifugal fans, fan motor, DX cooling coil, outer casing, filter, control and power panel with remote control etc. both inter connected with copper refrigerant pipe and drain pipe of required length as given, cabling and wiring, insulation with cross linked polyethelene foam, full charge of refrigerant gas and oil, M.S. base frame, supports etc. complete as per specifications and drawings. The cost shall also include angle iron stands for outdoor units. All ODU's to be placed on Roof Top support system , should be vibration free.
a) | Hi Wall Units (R-32 Refrigerant)
1.1.1 | 1.0 TR Unit (single ref.circuit) | Nos. | 1 | 52000 | 52000
1.1.2 | 1.5 TR Unit (single ref.circuit) | Nos. | 1 | 58000 | 58000
b) | Ductable Type (R-32 Refrigerant)
1.1.4 | 5.5 TR Unit (single ref.circuit) | Nos. | 1 | 110000 | 110000
| Sub-Total Part-'B' Rs. |  |  |  | 220000