## LOW SIDE
NAME OF PROJECT: LKO FOOD HALL AT LUCKNOW
HVAC WORK(LOW SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | EQUIPMENTS
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 24G sheet | sq.m | 40 | 2250 | 90000
| 26G sheet | sq.m | 5 | 2050 | 10250
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 24G sheet | sq.m | 5 | 1950 | 9750
3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1 | 14500 | 14500
4 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1 | 15500 | 15500
5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 1 | 12500 | 12500
6 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Return air Grilles without volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 2 | 9800 | 19600
7 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications:
| 15 mm thick | sq.m | 10 | 750 | 7500
8 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
| 19mm thick | sq.m | 40 | 850 | 34000
9 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications.
| 25mm Dia | Rmt | 5 | 950 | 4750
10 | Supply ,Installation ,Testing and commissioning of ERW heavy duty C Class MS pipes as per IS-1239 upto 6" dia. and as per IS-3589 above 6" dia. cut to required lengths and installed with all welded joints, complete with necessary pipe hot dip galvanized MS supports, GI hangers with rubber lined universal clamps and hangers , fittings like bends, elbows, tees, reducers, matching flanges, neoprene 6 mm thick gaskets, hot dipped galvanized nut & blots & washers ,PUF gutti with U clamp, socket and fittings for instruments and sensors connections etc. ERW pipes shall be with two coats of Zinc Chromate paint for anti-rust including all fittings like valves, flanges and unions, etc. Note : Pipe Measurement are in Pair (Supply + Return) . Quoted rates shall be inclusive of the cost of piping Insulation of Class O rated thermal insulations with one sided factory laminated glass clothed Nitrile Rubber insulation with density 45-60 kg/m3 with covered with two coats of UL Listed lag coating (Low VOC) Anti-fungal, Anti-microbial & vapour barrier for line item sealed with acrylic based food grade sealant.
| 32 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 10 | 2450 | 24500
11 | Providing and fixing in position following ball valves
11.1 | 32 mm dia valves | Nos. | 2 | 4500 | 9000
12 | Providing and fixing in position the following ‘Y’ Strainers :
12.1 | 32 mm dia strainers | Nos. | 1 | 5500 | 5500
13 | Supplying, installation, testing and commissioning of Auto air vents.
13.1 | 25 mm dia pipes | Nos. | 1 | 3500 | 3500
14 | Providing and fixing in position SS 304 the industrial dial type pressure gauges with gun metal valves. | Nos. | 2 | 7500 | 15000
15 | Providing and fixing in position SS 304 the mercury-in- glass industrial dial type thermometers. | Nos. | 2 | 6500 | 13000
16 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display & fan speed control, capable of providing individual space temperature control for cooling application. The controller shall produce a dual output to cooling coils in response to load change in rooms. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water duty . (minimum of 5 Deg F dead band ) | No. | 1 | 8500 | 8500
17 | Supply, installation, testing and commissioning of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC / 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. The minimum close off pressure actuator must be 1.5 times shut off head of pump 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes:
17.1 | 32 mm dia | No. | 1 | 7500 | 7500
18 | Supply, Installation, Testing and Commissioning of BMS compatible ultrasonic BTU Meter complete with flanged type water flow meter (pressure drop across water meter not exceeding 0.1 bar at the specified nominal flow rate), temperature sensors, LCD display panel, inbuilt Lithium battery backup with minimum six years life. The units shall be capable to calculate and store maximum values, display flow rates and temperature difference across supply and return. The quoted price shall be inclusive of necessary wiring, conduiting between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box. The size of the BTU meter is as under:
18.1 | 32 mm dia BTU Meter | No. | 1 | 65000 | 65000
19 | CONTROL PANEL FOR AHU (WITH DOL / SD STARTER)
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing & terminating into MCCB in each panel shall be provided by the electrical contractor.
All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included.
All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
The panel shall include the following components and accessories.
a. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
b. | DOL / SD starter as per HP ratings
c. | Terminal block for power distribution.
d. | Contactor, over load relay with built in single phasing protection.
e. | Phase indicating lights and indicating light for ON status.
f. | Digital voltmeter and digital ammeter with selector switches.
g. | Time delay relay for delayed automatic restart of air handling unit motor.
h | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
i | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
The number of AHU/ FAN control panels shall be as follows.
| 2 HP DOL Starter | No. | 1 | 28000 | 28000
GRAND TOTAL |  |  |  |  | 397850

## MAKE LIST
NAME OF PROJECT: LKO FOOD HALL AT LUCKNOW
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Air Handling Unit | Zeco/ Edgetech / Carrier/ Blue star / Waves
9 | M.S. Pipe upto 200 MM Dia. | AST / Jindal Hissar / Prakash Surya /Tata Steel
10 | UPVC Drain Piping | Prince / Supreme
11 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
12 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
13 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
14 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
15 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
16 | Cables | Polycab / Finolex / Hawells
17 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
18 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
19 | ESP Filter | Honeywell/Magneto/Trion
20 | Ball valve | Honeywell/Zoloto/Emerald /Advance Valve /Navtech (Castle
21 | Y Strainer | Emerald / Rapidcool
22 | Pressure Gauge | Emerald /Fiebig /H Guru
23 | Thermometer | Emerald /Fiebig /H Guru
24 | Auto Air Vent Valve | RB / Rapid Control
25 | PIBCV for AHU | Belimo / Danfoss / Honeywell / Schneider / Siemens
26 | Room Thermostat | Danfoss / Honeywell / Schneider / Siemens
27 | Starter | Siemens / Allen Bradley/ ABB / Schneider / L & T
28 | BTU Meter | Johnson Control / Honeywell / Kamstrup / Landis Gyr