## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
96050 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  | 0.00 | 0.00 |  | 0
96051 | a | AIR HANDLING UNIT CHW FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, Copper to MS adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet Outlet temp to be 8 13.5°C. AHUs shall be of following design parameters Capacity Tonnage ESP No. of USGPM (Cfm) TR (mm WG) Rows 11200 25 40 4 6 60 | No | 485309 | 1 | 28% | 485309
96052 | a | VRF FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with rated 3phase motor. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60-65dbA at 3m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium. AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, and vibration isolation pads. Scope also includes limit switch with lights in AHU. Cooling Coil section with AHRI certified Coil (0.15mm AL 13 FPI fins 12.7 mm OD 27 SWG Cu Tube) suitable for VRF Outdoor Unit (R410a refrigerant). AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). AHUs shall be of following design parameters Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows 10500 27 40 4 6 | No. | 475825 | 1.00 | 28% | 475825
96053 | a | SUPPLY OF VRF OUT-DOOR UNITS Supply of air cooled variable refrigerant flow modular type ODUs each comprising of multiple rotary scroll compressors fully inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. TheODUs shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities OUTDOOR UNITS 34 HP at site conditions. Note The unit shall be selected taking indoor and ambient deration, refrigerant pipe length deration in to account. | No. | 559550 | 1.00 | 28% | 559550
96054 |  | AHU CONTROLLER AND EEV KIT - Supply of AHU Controller, Electronic Expansion Valve (EEV) Kit and all other necessary accessories to connect with VRF ODU s. | No. | 75050 | 1.00 | 28 | 75050
96055 |  | FRAME WORK - Supply, fabrication and installation of PCC Siporex blocks for AHU support. AHU framework shall be part of AHU supply. Each AHU shall require 9nos. of blocks. | Sets |  | 3.00 | civil work | 0
96056 |  | SPARE FILTER - One set of MERV 8 throw away type filters to be provided for all AHUs. These filters will be used for commissioning. Original set of filters will be installed as instructed by Architect Consultants. | Sets | 45600 | 2.00 | 28% | 91200
96057 |  | GENERAL NOTES a. Fan outlet velocity - 1600 FPM b. Contractor shall submit static pressure calculation for all above units to Client Consultant. c. Any change in motor HP shall be made at no extra cost to client. d. Fan efficiency shall be minimum 75% e. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.00 |  | 0
96058 |  | VENTILATION SYSTEM INLINE CIRCULAR FAN SITC of Inline Circular fan (silent type) with speed control, direct drive package - motor with outlet dampers, fan inlet outlet flexible connection, hanging arrangement with vibration isolators etc. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor. Motor efficiency IE2 IE3, AMCA Certification and Noise levels at 1m distance to be specified.The fans shall have BMS Compatibility. |  |  | 0.00 |  | 0
96059 | a | 700 CFM @ 25 mmwg ESP | Nos | 58900 | 2.00 | 28% | 117800
96060 | b | 100 CFM @ 15 mmwg ESP | No | 46075 | 1.00 | 28% | 46075
96061 |  | NOTES a. Contractor shall submit static pressure calculation for all above units to Client Consultant. b. Any change in motor HP shall be made at no extra cost to client. c. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.00 |  | 0
[6 empty] | TOTAL | 1850809