## SUMMARY SHEET
FOOD HALL AT LUCKNOW AIRPORT
SUMMERY SHEET FOR ELECTRICAL WORKS
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | TOTAL AMOUNT IN Rs.
A | ELECTRICAL
1 | PANELS, SWITCHGEAR & DISTRIBUTION BOARDS | 36000
2 | MV CABLES | 24500
3 | RACEWAY & CABLE TRAY
4 | POINT WIRING | 297725
5 | MODULAR SWITCHES | 50600
6 | GENERAL EARTHING | 2550
7 | LIGHT FIXTURES ONLY INSTALLATION | 227500
8 | MISCELLANEOUS | 4800
9 | CCTV | 181040
10 | FAS
11 | UPS | 42000
| TOTAL FOR ELECTRICAL WORKS | 866715

## 1.PANEL & DB
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR PANELS & DISTRIBUTION BOARDS - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | REVISED QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
2.2 | DISTRIBUTION BOARDS
2.2.2 | 6 WAY V-TPN DB - LPDB | Nos. | 1 | 36000 | 36000
Incomer : 63A, FP, MCB, 10kA: 1 Nos
Sub Incomer : 32A, DP, RCCB, 100mA: 3 Nos
Outgoings : 6/10/16 A SP MCB "C" Type - 18 Nos.
| TOTAL FOR DISTRIBUTION BOARDS |  |  | Rs. | 36000

## 2.MV CABLES
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR MV CABLES - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
2 | MV CABLES
2.1 | POWER CABLING
Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE FRLS armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.3 | CU Flexible Cables
a | 4C x 6 Sq.mm. | Mtr. | 30 | 650 | 19500
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
a | 3.5C x 70 Sq.mm. AL | Nos. | 2 | 1450 | 2900
m | 4C x 6 Sq.mm. | Nos. | 2 | 1050 | 2100
TOTAL FOR POWER CABLE TERMINATION
| TOTAL FOR CABLES & TERMINATION |  |  | Rs. | 24500

## 4.POINT WIRING
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR POINT WIRING - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
4 | POINT WIRING
Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr.
The secondary/Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr.
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
The Length shall be paid as per the actual measurements & as per following manner.
4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required from the above switch board. Rates shall exclusive of Switches & Switch Box. (FROM SB TO LIGHT)
4.2.1 | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 15 | 2250 | 33750
4.2.3 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 6 | 2450 | 14700
4.3 | Same as item No. 4.2.1 & 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 12 | 1850 | 22200
4.4 | Same as item No. 4.2.3 & 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing For Emergency Light | Nos. | 8 | 2150 | 17200
4.5.1 | First point controlled by existing MCB in D.B. | Nos. | 10 | 2650 | 26500
4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 30 | 1850 | 55500
4.8 | Wiring for UPS/Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 200 | 325 | 65000
4.9 | Wiring for UPS/Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 125 | 355 | 44375
4.10.1 | 20 mm dia GI Conduit | Mtr. | 100 | 185 | 18500
| TOTAL FOR POINT WIRING |  |  | Rs. | 297725

## 5.SWITCHES
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR MODULAR SWITCHES - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
5 | MODULAR SWITCHES
5.1 | Supply, installation, testing & commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches & earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.(Make- Legrand Aretor Series)
5.1.1 | 6A One Way Switch | Nos. | 22 | 1050 | 23100
5.1.2 | 6A 5 pin Socket - 1Nos. & 6A Switch - 1Nos. | Nos. | 22 | 1250 | 27500
| TOTAL FOR MODULAR SWITCHES |  |  | Rs. | 50600

## 6.GEN EARTHING
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR GENERAL EARTHING - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
6 | GENERAL EARTHING
6.2 | Supplying and erecting bare Copper conductor of following sizes
6.2.1 | 8 SWG | Mtr. | 30 | 85 | 2550
| TOTAL FOR GENERAL EARTHING |  |  | Rs. | 2550

## 7.LIGHT FIXTURE
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR LIGHT FIXTURE INSTALLATION - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
7 | LIGHT FIXTURES INSTALLATION
7.1 | Receiving from Store, Installation, testing & commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook/Rods as per final approval from Architect/Client/Consultant
7.1.1 | DOME LIGHT | Nos. | 13 | 8500 | 110500
7.1.2 | CYLINRICAL SURFACE MOUNT LIGHT | Mtr. | 36 | 3250 | 117000
| TOTAL FOR LIGHT FIXTURE |  |  | Rs. | 227500

## 8.MISC
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR MISCLLANEOUS WORKS - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R0 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
8 | MISCELLANEOUS WORKS
8.1 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 | 1450 | 1450
8.2 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 | 3350 | 3350
| TOTAL FOR MISCELLANEOUS WORKS |  |  | Rs. | 4800

## 9. CCTV
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR CCTV - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R1 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
1 | CCTV System
1.1 | 2 Megapixel Fixed Lens Camera IR Dome Type: 1/2.8"Progressive Scan CMOS, 1920 × 1080 at 25fps, 2.8mm Fixed lens, 0.028 Lux at F1.2, ICR, ONVIF, support H.265, H.264, MJPEG, 120db WDR, 3D Digital Noise Reduction, Three individually configurable stream, 12 VDC & PoE, IR range: 40m, Support on-board storage up to 128 GB (SD card not included), IP67, IK10, Edge Anlalytics- Line crossing detection, Intrusion detection, Motion detection, Scene change detection, video tampering, UL, CE, FCC certified. | Nos. | 4 | 4800 | 19200
1.5 | NVR 16 Channel: Connect Up to 16 IP Cameras, Dual OS, Up to 8 Megapixels Resolution, HDMI output with 4k output and VGA output with 2MP Output , Support H.265,H.264, MJPEG, Incoming Bandwidth 160 Mbps, 4 SATA Hard Disks, ANR Technology, 2 SATA interfaces for 2 HDDs and capacity of each HDD upto 6TB, 2 USB at least 1 × USB with 3.0, Serial interface:1 RS-485, 1 RS-232, Alarm I/O 16/4, 2 RJ-45 10 /100/1000 Mbps self-adaptive Ethernet interface, Multiple network monitoring: Web viewer, CE, FCC, UL certified. | Nos. | 1 | 22500 | 22500
1.6 | 16 Port Network Switch Gigabit POE: 16 × gigabit PoE ports, 1 × gigabit RJ45 port, and 1 × gigabit SFP fiber optical port, IEEE 802.3at/af standard | Nos. | 1 | 3200 | 3200
1.7 | CAT 6 Connector | Nos. | 8 | 950 | 7600
1.8 | Hard Disk 6 TB | Nos. | 2 | 18500 | 37000
1.9 | Suplly & installation of Computer system as required | Nos. | 1 | 35500 | 35500
1.1 | Installation/labour charges | Job | 1 | 10000 | 10000
1.11 | Supply, Drawing and Testing of 4 pair ,100 Ohm, 24 AWG UTP Cat 6 Cable as per latest amendments of TIA / EIA 568 B.2 specifications for Data / Telephone points in existing MS /PVC conduits including making connections to Information outlets and patch panels with ferruling at both ends for identification with necessary tools for punching ,stripping crimping and testing as required | Mtr | 80 | 185 | 14800
1.12 | Supply and laying of HDMI Cabel | Nos. | 1 | 9500 | 9500
1.13 | Supply and Laying of RIGID PVC Medium Duty Conduits ISI marked conduits complete with accessories such as bends, junction boxes, pull boxes etc., in recess or on surface including cutting chases in the walls/floors and making good the same complete as required.
1.13.1 | 32 mm dia | RM |  |  | 0
1.13.2 | 25 mm dia | RM | 32 | 195 | 6240
1.14 | Supply , Installation, Testing and Comissioning of Wall mounted Communication rack with glass doors, handles ,lock , Top and Bottom Cable entries, Supports for mounting rack on wall , Cable managers, one Fan, Equipment mounting hardware, power supply box for supplying power to switches, fans etc along with earth continuity kit, Mcb, indicator, moulded power supply cable .
1.14.2 | 12U(44 mm ) wall mounted | Nos. | 1 | 15500 | 15500
| TOTAL FOR MISCELLANEOUS WORKS |  |  | Rs. | 181040

## 11.UPS
FOOD HALL AT LUCKNOW AIRPORT
BILL OF QUANTITIES FOR UPS - R0
DATE: 02.FAB.2024
SR. NO. | DESCRIPTION | UNIT | TOTAL QTY. R1 | RATE IN Rs. | TOTAL AMOUNT IN Rs.
11 | UPS System
| Supply,Installation, testing and commissioning of following type of Online UPS / Inverter as per drawings and specifications with all other accessories. | Nos. | 1 | 42000 | 42000
Online UPS
1.2.0KVA UPS
12V DC/25AH maintenance free batteries for 30 minutes battery backup.
Input supply voltage:-230-250 Volts
Output voltage:-220-240V+/-1%
Voltage Regulation:-Less than or equal to +/- 1%
Output frequency :-50 Hz +/- 0.05 Hz
Type of cooling :-Forced air cooled
Invertor Efficiency :-Better than 85%
Output Power factor :-0.8
| TOTAL FOR UPS |  |  | Rs. | 42000

## APPROVED MAKES
1. LIST OF APPROVED MAKES FOR ELECTRICAL EQUIPMENT & MATERIALS
(All major equipment/Materials shall be tested and approved by CPRI/ERDA (NABL accredited laboratory) and shall carry ISI mark. All manufacturer shall possess valid ISO certificate)
Sl. No. | Equipment & materials | Makes
1 | Low voltage switchgear enclosure (415v) (iec 61439 compliant) & switchgears | Schneider / legrand / siemens / abb / l&t
2 | Ups system (uninterruptable power supply) (415/230v) | Apc-schneider /eaton / socomec / vertiv
3 | Vrla smf battery | Excide / amararaja / rocket
4 | Dbs | Legrand - ekinoxe / schneider - acti9 / siemens / abb
5 | Vfd (variable frequency drive) | Allen bradley / alstom / danfoss / siemens/ abb/ l&t yaskawa/honeywell
6 | Motor starter | Abb / schneider / siemens / l&t
7 | Cable (415v) | Rpg/ finolex / universal /havells
8 | Disconnect switch | Schneider / abb / siemens / l&t
9 | Wires/copper flexible cable | Finolex / havells / rajnigandha / rr kabel
10 | Raceways and junction boxes | Mk / legrand / obo bettermann
11 | Cable trays | Obo bettermann / legrand / indiana / profab
12 | Spd (surge arraster) | Obo / legrand / schneider
13 | Meters (analog) | Meco / rishabh / nippen / conserve / ae
14 | Meters (digital) | Ae / schneider / nippen / conserve / l&t
15 | Energy meter , load manager | Schneider (em 6400ng or equivalent) / l&t / nippen / hpl / socomec
16 | Indicating lamps | Schneider / l & t / salzer
17 | Rotary switch | Siemens / keycee / salzer / meco
18 | Push button and push button set | Siemens / schneider electric / l & t / legrand / c&s / abb
19 | Selector switch | Keycee / salzer / meco
20 | Gi conduits and accessories | Bharat / supreme/bec
21 | Control transformer [ pt / ct ] | Ashmor / kappa / elmex
22 | Fire barrier | Obo bettermann / hilti / 3m
23 | Terminal block | Essen / connect well /elmex
24 | Control switch | Alstom/kaycee/switron
25 | Hrc fuse | Siemens /l&t /alstom/s&s /cgl /ge /standard
26 | Limit switch | Siemens /essen /bch /ind syndicate/epcc(kakku)
27 | Elr with cbct | Kalpa / jvc / prok dv’s
28 | Overload relays with built in single phase preventer | Siemens/ abb/ l&t / schneider
29 | Power/aux. Contactor | L&t / schneider
30 | Auxiliary relays | Siemens / ge alstom / abb / jvs / prok dv’s
31 | Protection relay - electromagnetic type | Areva
32 | Protection relay - numeric type | Areva / siemens / l&t / sel
33 | 1.1kv, grade lt fire survival cables | Anchor/finolex/ havells / kei/ kec
34 | Signal cable | Enercon / lapp india / system tek / caliplast / eminent
35 | Cable lugs | Dowell’s / 3d / hex / jainson / comet / hmi
36 | Bimetallic lugs | Hmi / hex / connect
37 | Cable glands | 3d / comet / hmi
38 | Lt cable jointing kits(cold curing) | Reychem/3m
39 | Pvc tape | Steel grip / isi apprved
40 | Pvc junction box | Hensel / clipsal / spelsberg / scame / sintex
41 | Ceiling fan / exhaust fan | Crompton / bajaj / orient / havells
42 | Electric timer | Siemens / legrand / l&t / meco /telemechanique
43 | Connectors (colours as per phase & neutral) | Wago / phoenix contact/ connectwell
44 | Industrial socket with mcb | Legrand / schneider/mennekes
45 | Modular switches, sockets & other accessories | Mk – blenze / legrand-arteor / schnedier-zencelo / norisys / l&t anchor - woods/ hpl - smart / c&s-primo / havells - crabtree
46 | Metal clad socket with mcb | Legrand / hensel / schneider / scame / spelsberg
47 | Public spaces light fixtures | Philips/ lighting technology/ regent/ zumtobel/ jaquar/ iguzzini/ erco / endo / bega / lumenpulse or
As per final approval of fixture by architects.
48 | Insulating mat | Jyoti / premier polyfilm limited (electromat)/
49 | Eathing material | Obo/jef/cape