**KUBER GAS TECH**

 Ref: MNGL/PNG/2023-24/101 Date. 11/01/2024

## **Subject - Pneumatic Testing of PNG Gas Pipeline.**

## This is to inform that we have done fabrication & erection of PNG Gas pipeline within your Plant as follows.

## **Plant Name:** M/s. THE IRISH HOUSE FOOD AND BEVERAGES PRIVATE LIMITED

## **Address:** T-26, 3RD FLOOR, PHOENIX MALL OF MILLENNIUM, WAKAD, PUNE – 411057.

## **contractor Company Name**: M/s. KUBER GAS TECH

## **Connection:** MNGL

1. Pipe line Size : 40NB CS SCH 40 PIPELINE
2. Length : PIPING LENGTH 2.00 MTRS
3. MOC of Pipe : S.S Seamless SCH 40 as per ASTM A106 Gr.8
4. Work ing Pressure : 1.50 Kg/Cm2
5. Design Pressure : 10 KG/ Cm2
6. Tested Pressure : 6.5 Kg/ Cm2
7. Testing Method : Pneumatic Testing with Compressed Air.
8. Date of Testing :09/01/2024

|  |  |  |  |
| --- | --- | --- | --- |
| **TEST DATE** | **TIME** | **TESTING PRESSURE** | **REMARK** |
| 09/01//2024 | 09.40 PM | 6.5 KG/CM2 | FOUND OK |
| 10/01//2024 | 10.40 AM | 6.5 KG/CM2 | FOUND OK |

We hereby certify that the above PNG Gas Pipeline has been successfully tested at 6.5 kg/cm2 for the duration of more than 24 hours.

RESULT: NO LEAKAGE & NO PRESSURE FOUND

#  FOR KUBER GAS TECH

#  SR. TECHNICIAN/ENGINEER

**Residential and Commercial Reticulated Gas Pipe Line Fitting & Kitchen Equipment**

**Add: GFF1, Bldg no 4, Techno Cidade, Chogm Road, Porvorim, Goa-403521.**

**Ph.: 08322452704/ 9823046425/ 9561070324/**

**Email:** [**kubergastech@gmail.com**](file:///C%3A%5CUsers%5Cwin%5CAppData%5CRoaming%5CMicrosoft%5CWord%5Ckubergastech%40gmail.com)**.**